## Measure units
|  |  | N. of decimal places |  |  |  | Multiplier | Min val | Max val
Measure unit Tool/Controller | Bacnet name | Bacnet enum | SxTool | W ser. | Bacnet | Modbus | Modbus | All | All
Unknown Unit | - | - | 0 | 0 | 0 | 0 | 1 | 0:00 | 10000.0
Celsius Degrees | UNIT_DEGREES_C | 62 | 1 | 1 | 1 | 1 | 0:01 | -40.0 | 80:00
Fahrenheit Degrees | UNIT_DEGREES_F | 64 | 1 | 1 | 1 | 1 | 0:01 | -40.0 | 176:00
Parts Per Million | UNIT_PARTS_PER_MILLION | 96 | 0 | 0 | 0 | 0 | 1 | 0:00 | 1000000
Meters Per Second | UNIT_METERS_PER_SECOND | 74 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 25:00
Humidity | UNIT_RELATIVE_HUMIDITY | 29 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 100:00
Seconds | UNIT_SECONDS | 73 | 0 | 0 | 0 | 0 | 1 | 0:00 | 60:00
Minutes | UNIT_MINUTES | 72 | 0 | 0 | 0 | 0 | 1 | 0:00 | 60:00
Hours | UNIT_HOURS | 71 | 0 | 0 | 0 | 0 | 1 | 0:00 | 24:00
Hertz | UNIT_HERTZ | 27 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 100:00
Lux | UNIT_LUXES | 37 | 0 | 0 | 0 | 0 | 1 | 0:00 | 20000.0
Ampere | UNIT_AMPERES | 3 | 3 | 3 | 3 | 3 | 0.001 | 0:00 | 1000:00
Milliampere | UNIT_MILLIAMPERES | 2 | 2 | 2 | 2 | 2 | 0:01 | 0:00 | 1000:00
Volt | UNIT_VOLTS | 5 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 400:00
Kwh | UNIT_KILOWATT_HOURS | 19 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 99999999.9
Watt | UNIT_WATTS | 47 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 230000.0
KiloWatt | UNIT_KILOWATTS | 48 | 0 | 0 | 0 | 0 | 1 | 0:00 | 230000.0
VA | UNIT_VOLT_AMPERES | 8 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 230000.0
VAR | UNIT_VOLT_AMPERES_REACTIVE | 11 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 230000.0
KVAR | UNIT_KILOVOLT_AMPERES_REACTIVE | 12 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 99999999.9
VARh | UNIT_WATT_HOURS_REACTIVE | 203 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 99999999.9
KVARh | UNIT_KILOWATT_HOURS_REACTIVE | 204 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 99999999.9
PF | UNIT_POWER_FACTOR | 15 | 3 | 3 | 3 | 3 | 0.001 | -0.99 | 0.06875
Percentage | UNIT_PERCENT | 98 | 1 | 1 | 1 | 1 | 0:01 | 0:00 | 100:00
Number | UNIT_NO_UNITS | 95 | 3 | 3 | 3 | 3 | 0.001 | 0:00 | 100000.0
Angular Degrees | UNIT_DEGREES_ANGULAR | 90 | 1 | 1 | 1 | 1 | 0:01 | -360 | 360:00
Radians | UNIT_RADIANS | 103 | 0 | 0 | 0 | 0 | 1 | -1.0 | 1:00
Cubic Meters | UNIT_CUBIC_METERS | 80 | 0 | 0 | 0 | 0 | 1 | 0:00 | 99999999.9
WM | Custom Potenza media | 500 | 1 | 1 | - | 1 | 0:01 | 0:00 | 230000.0
H2o Hot Cubic Meters | Custom | 501 | 0 | 0 | - | 0 | 1 | 0:00 | 99999999.9
H2o Cold Cubic Meters | Custom | 502 | 0 | 0 | - | 0 | 1 | 0:00 | 99999999.9
H2o Hot Kwh | Custom | 503 | 0 | 0 | - | 0 | 1 | 0:00 | 99999999.9
Gas Cubic Meters | Custom | 504 | 0 | 0 | - | 0 | 1 | 0:00 | 99999999.9
Em Hours | Custom | 505 | 2 | 2 | - | 2 | 0:01 | 0:00 | 100000.0
Em Counter | Custom | 506 | 3 | 3 | - | 3 | 0:01 | 0:00 | 1000000.0

## Info Modbus
| Parameter name | Register type | Relative address (word) | Word lenght Modbus | ModBus Function | Data info | Data type | Measure Unit | min | max | error
LIGHT ON/OFF
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF bit11 = PIR presence all other bits: reserved | UInt16 | Unknown Unit
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Lux Interval Name | IR | 3 | 1 | 4 | None = -1 Default = 0 Night = 10 Day = 20 | UInt16 | Number | 0 | 5000
| Energy save timer | IR | 4 | 2 | 4 |  | UInt32 | Seconds | 0 | 43200 (720min)
| Lux | IR | 6 | 2 | 4 |  | UInt32 | Lux | 0 | 20000 | 7FFFFFFFh
| Function STATE | HR | 0 | 1 | 3 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
PARAMETERS | Energy save delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 43200 (720min)
| Lux thereshold | HR | 4 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| cloud filter | HR | 5 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Action on night | HR | 6 | 1 | 3 | -1 = no action 0 = OFF 1 = ON | Int16 | Percentage
| Action on day | HR | 7 | 1 | 3 | -1 = no action 0 = OFF 1 = ON | Int16 | Percentage
| Automation enable delay | HR | 8 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Lux Disable Pir during day time | HR | 10 | 1 | 3 | Il luxmetro disabilita il in condizione giorno 0 = False 1 = True | UInt16 | Unknown Unit
| Allow Pir to Switch ON | HR | 11 | 1 | 3 | Il pir e' abilitato ad accendere la luce 0 = False 1 = True | UInt16 | Number
INTRUDER MAIN FUNCTION
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | Bit8 = Reset Bit9 = Override decativated (without alarm) Bit10 = Override alarm | UInt16 | Unknown Unit
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | 0 = Deactivated (in disarmed) 1 = Activated (in disarmed) 2 = Arming (without alarm) 3 = All armed (without alarm) 4 = Armed (without alarm) 5 = Warning (arming with alarm) 6 = Disarming (disarming time in progress) 7 = Alarm 8 = Waiting acknowledgment | UInt16 | Unknown Unit
PARAMETERS | Automantion enable delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
INTRUDER ZONE ALARM
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | Bit8 = Disable Bit9 = Override alarm Bit10 = Override decativated (without alarm) | UInt16 | Unknown Unit
| Arming TIMER | IR | 1 | 1 | 4 |  | UInt16 | Seconds | 0 | 300
| Disarming TIMER | IR | 2 | 1 | 4 |  | UInt16 | Seconds | 0 | 300
| Function STATE | HR | 0 | 1 | 4 | 0 = Deactivated (in disarmed) 1 = Activated (in disarmed) 2 = arming (without alarm) 3 = warning (arming with alarm) 4 = armed 6 = pre alarm (disarming time in progress) 7 = alarm | UInt16 | Unknown Unit
PARAMETERS | Arming delay | HR | 2 | 1 | 3 |  |  | Seconds | 0 | 300
| Disarming delay | HR | 3 | 1 | 3 |  |  | Seconds | 0 | 300
WATER ALARM
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Unknown Unit
| Reset timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Water alarm state | IR | 3 | 1 | 4 | 0 = Armed 1 = Active 2 = Disabled | UInt16 | Number
| Function STATE | HR | 0 | 1 | 4 | 0 = No alarm 1 = Alarm | UInt16 | Unknown Unit
COMMANDS | SET | HR | - | 1 | 3 | 0 = trigger reset 1 = stop reset 2 = toggle reset
PARAMETERS | Reset delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
SMOKE ALARM
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Unknown Unit
| Reset timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Smoke alarm state | IR | 3 | 1 | 4 | 0 = Armed 1 = Active 2 = Disabled | UInt16 | Number
| Function STATE | HR | 0 | 1 | 4 | 0 = No alarm 1 = Alarm | UInt16 | Unknown Unit
PARAMETERS | Reset delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
SIREN
STATUS | Siren timer | IR | 0 | 2 | 4 |  | UInt32 | Seconds | 0 | 600
| Function STATE | HR | 0 | 1 | 4 | 0=OFF 1=ON | UInt16 | Unknown Unit
COMMANDS | SET | HR | - | 1 |  | 0 = trigger reset
PARAMETERS | Siren delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 600
| Siren delay on | HR | 4 | 2 | 3 |  | UInt32 | Seconds | 0 | 60
| Siren delay off | HR | 6 | 2 | 3 |  | UInt32 | Seconds | 0 | 60
ROLLERBLIND (without tilt)
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Full UP bit10 = Full DOWN all other bits: reserved | UInt16 | Unknown Unit
| Wind Interval Name | IR | 1 | 1 | 4 | Default = 0 Weak Wind = 1000 Strong Wind = 1010 | UInt16 | Number
| Lux Interval Name | IR | 2 | 1 | 4 | Lux Threshold 1 = 100 Lux Threshold 2 = 110 Lux Threshold 3 = 120 Lux Threshold 4 = 130 Lux Threshold 5 = 140 Lux Threshold 6 = 150 | UInt16 | Number
| Wind speed value | IR | 3 | 1 | 4 |  | UInt16 | Meters per seconds | 0.0 | 10.0 | 7FFFFFFFh
| Movement Position | IR | 4 | 1 | 4 |  | UInt16 | Percentage | 0 | 100 | 7FFFFFFFh
| LUX | IR | 5 | 2 | 4 |  | UInt32 | Lux | 0 | 20000 | 7FFFFFFFh
| Automation enable timer | IR | 7 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | Stato Running motore 0 = Stop 1 = Moving 2 = Moving Up 3 = Moving Down 6 = resetting Up 7 = resetting Down
PARAMETERS | Strong wind | HR | 2 | 1 | 3 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Weak wind | HR | 3 | 1 | 3 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Action weak wind ON | HR | 4 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Action weak wind OFF | HR | 5 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Weak wind cloud filter | HR | 6 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Strong wind cloud filter | HR | 7 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Lux1 threshold | HR | 8 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Action Lux1 | HR | 9 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Lux2 threshold | HR | 10 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Action Lux2 | HR | 11 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Lux3 threshold | HR | 12 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Action Lux3 | HR | 13 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Lux4 threshold | HR | 14 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Action Lux4 | HR | 15 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Lux5 threshold | HR | 16 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Action Lux5 | HR | 17 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Action Lux6 | HR | 19 | 1 | 3 |  | UInt16 | Percentage | 0 | 100
| Lux cloud filter | HR | 20 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Automation enable delay | HR | 21 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
ROLLERBLIND (with tilt)
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Full UP/ TILT -> 0 bit10 = Full DOWN/ TILT -> 100 all other bits: reserved | UInt16 | Unknown Unit
| Wind Interval Name | IR | 1 | 1 | 4 | Default = 0 Weak Wind = 1000 Strong Wind = 1010 | UInt16 | Number | 0 | 5000
| Lux Interval Name | IR | 2 | 1 | 4 | Lux Threshold 1 = 100 Lux Threshold 2 = 110 Lux Threshold 3 = 120 Lux Threshold 4 = 130 Lux Threshold 5 = 140 Lux Threshold 6 = 150 | UInt16 | Number | 0 | 5000
| Wind speed value | IR | 3 | 1 | 4 |  | UInt16 | Meters per seconds | 0.0 | 10.0 | 7FFFFFFFh
| Tilt and Movement Position | IR | 5 | 1 | 4 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| LUX | IR | 6 | 2 | 4 |  | UInt32 | Lux | 0 | 100000
| Automation enable timer | IR | 8 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | Stato Running motore 0 = Stop 1 = Moving 2 = Moving Up 3 = Moving Down 6 = resetting Up 7 = resetting Down | UInt16 | Unknown Unit
PARAMETERS | Strong wind speed for safety position | HR | 2 | 1 | 3 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Wind speed threshold | HR | 3 | 1 | 3 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Wind speed above threshold moves to position | HR | 4 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Wind speed below threshold moves to position | HR | 6 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Wind threshold cloud filter | HR | 8 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Strong wind speed cloud filter | HR | 9 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Lux1 threshold | HR | 10 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Position on threshold 1 | HR | 11 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Lux2 threshold | HR | 13 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Position on threshold 2 | HR | 14 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Lux3 threshold | HR | 16 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Position on threshold 3 | HR | 17 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Lux4 threshold | HR | 19 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Position on threshold 4 | HR | 20 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Lux5 threshold | HR | 22 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Position on threshold 5 | HR | 23 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage | -1 | 100
| Position on threshold 6 | HR | 26 | 1 | 3 | MSWord = %Tilt, LSWord = %Movement, 0=0%, 255 = -1 (no action) | UInt16 | Percentage
| Lux cloud filter | HR | 27 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Automation enable delay | HR | 28 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
WINDOW
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = override 100% bit10 = override 0% all other bits: reserved | UInt16 | Unknown Unit
| Wind | IR | 1 | 1 | 4 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Wind Interval Name | IR | 2 | 1 | 4 | Default = 0 Weak Wind = 1000 Strong Wind = 1010 | UInt16 | Number
| Temperature | IR | 3 | 2 | 4 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0
| Temperature Interval Name | IR | 5 | 1 | 4 | Default = 0 Low Temperature = 2000 High Threshold = 2010 | UInt16 | Number
| Movement Position | IR | 6 | 1 | 4 |  | UInt16 | Percentage | 0 | 100
| Automation enable timer | IR | 7 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | Stato Running motore 0 = Stop 1 = Moving 2 = Moving Up 3 = Moving Down 6 = resetting Up 7 = resetting Down | UInt16 | Unknown Unit
PARAMETERS | Strong wind speed for safety position | HR | 2 | 1 | 3 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Wind speed threshold | HR | 3 | 1 | 3 |  | UInt16 | Meters per seconds | 0.0 | 10.0
| Wind speed above threshold moves to position | HR | 4 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Wind speed below threshold moves to position | HR | 5 | 1 | 3 |  | UInt16 | Percentage | -1 | 100
| Weak wind cloud filter | HR | 6 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Strong wind cloud filter | HR | 7 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Temperature1 threshold | HR | 8 | 1 | 3 |  | UInt16 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0
| Action temp1 | HR | 9 | 1 | 3 |  | Int16 | Unknown Unit | -1 | 100
| Temperature2 threshold | HR | 10 | 1 | 3 |  | UInt16 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0
| Action temp2 | HR | 11 | 1 | 3 |  | Int16 | Unknown Unit | -1 | 100
| Temperature cloud filter | HR | 12 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Automation enable delay | HR | 13 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
TEMPERATURE ZONE
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | Bit8 = Disable Bit9 = not used Bit10 = not used Bit11 =not used Bit12 = Override Heating OFF Bit13 = Override Cooling OFF Bit14 = Override Heating ON Bit15 = Override Cooling ON | UInt16 | Number
| Tx_Heat selection | IR | 1 | 1 | 4 | 0 = OFF 1 = T1 2 = T2 3 = T3 | UInt16 | Number
| Tx_Cool selection | IR | 2 | 1 | 4 | 0 = OFF 1 = T1 2 = T2 3 = T3 | UInt16 | Number
| Working Mode (from configuration) | IR | 3 | 1 | 4 | 1 = Heating 2 = Cooling 3 = Heating & Cooling | UInt16 | Number
| Troom | IR | 4 | 2 | 4 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0 | 7FFFh
| Tsys | IR | 6 | 2 | 4 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0 | 7FFFh
| Texternal | IR | 8 | 2 | 4 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0 | 7FFFh
| Automation enable timer | IR | 10 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Output value in heating mode | IR | 12 | 2 | 4 |  | Int32 | Number
| Output value in cooling mode | IR | 14 | 2 | 4 |  | Int32 | Number
| Function STATE | HR | 0 | 1 | 4 | 0 = OFF 1 = HEAT ON 2 = COOL ON 3 = HEAT & COOL ON | UInt16 | Unknown Unit
| T1 Heat setpoint | HR | 2 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | Tmin | Tmax
| T2 Heat setpoint | HR | 4 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | Tmin | Tmax
| T3 Heat setpoint | HR | 6 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | Tmin | Tmax
| T1 Cool setpoint | HR | 8 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | Tmin | Tmax
| T2 Cool setpoint | HR | 10 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | Tmin | Tmax
| T3 Cool setpoint | HR | 12 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | Tmin | Tmax
| Automation enable delay | HR | 18 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
| T1 Heat setpoint deadband | HR | 20 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees
| T2 Heat setpoint deadband | HR | 22 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees
| T3 Heat setpoint deadband | HR | 24 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees
| T1 Cool setpoint deadband | HR | 26 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees
| T2 Cool setpoint deadband | HR | 28 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees
| T3 Cool setpoint deadband | HR | 30 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees
HEAT TEMPERATURE SYSTEM
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Number
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | 0 = DEACTIVATED 1 = ACTIVATED | UInt16 | Unknown Unit
COMMANDS | SET | HR |  | 1 | 3 | 0 = Deactive 1 = Active 2 = Toggle 1000 = Activate automatism disable (with timeout) 1001 = Deactivate automatism disable
| Automation enable delay | HR | 2 | 2 | 16 |  | UInt32 | Seconds | 0 | 3540 (59min)
COOL TEMPERATURE SYSTEM
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Number
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | 0 = DEACTIVATED 1 = ACTIVATED | UInt16 | Unknown Unit
COMMANDS | SET | HR |  | 1 | 3 | 0 = Deactive 1 = Active 2 = Toggle 1000 = Activate automatism disable (with timeout) 1001 = Deactivate automatism disable
| Automation enable delay | HR | 2 | 2 | 16 |  | UInt32 | Seconds | 0 | 3540 (59min)
TIMER (Delay)
STATUS | Timer type | IR | 0 | 1 | 4 | 0 = Delay 1 = Interval 2 = Oscillator | UInt16 | Number
| Delay On Timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 86400
| Delay Off Timer | IR | 3 | 2 | 4 |  | UInt32 | Seconds | 0 | 86400
| Function STATE | HR | 0 | 1 | 4 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
PARAMETERS | Delay On delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 86400
| Delay Off delay | HR | 4 | 2 | 3 |  | UInt32 | Seconds | 0 | 86400
TIMER (Recycling)
STATUS | Timer type | IR | 0 | 1 | 4 | 0 = Delay 1 = Interval 2 = Oscillator | UInt16 | Number
| Delay On Timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 86400
| Delay Off Timer | IR | 3 | 2 | 4 |  | UInt32 | Seconds | 0 | 86400
| Function STATE | HR | 0 | 1 | 4 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
COMMANDS | SET | HR | 1 | 1 | 3 | 0 = Reset 1 = Trigger
PARAMETERS | Delay On delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 86400
| Delay Off delay | HR | 4 | 2 | 3 |  | UInt32 | Seconds | 0 | 86400
TIMER (Interval)
STATUS | Timer type | IR | 0 | 1 | 4 | 0 = Delay 1 = Interval 2 = Oscillator | UInt16 | Number
| Delay Off Timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 86400
| Function STATE | HR | 0 | 1 | 4 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
PARAMETERS | Delay Off delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 86400
ANALOGUE COMPARATOR
STATUS | Control type | IR | 0 | 1 | 4 | 2 = Lower Than 3 = Higher Than 6 = Inside Interval 7 = Outside Interval | UInt16 | Number
| Analogue Input Value | IR | 1 | 2 | 4 |  | Int32 | (dynamic) | -65536 | 65536
| Delay On Timer | IR | 3 | 2 | 4 |  | UInt32 | Seconds | 0 | 600
| Delay Off Timer | IR | 5 | 2 | 4 |  | UInt32 | Seconds | 0 | 600
| Function STATE | HR | 0 | 1 | 4 | Valori di Default: 0 = OFF 1 = ON | UInt16 | Unknown Unit
PARAMETERS | Reference1 | HR | 1 | 2 | 3 | dp depend by the input variables, range is signed word | Int32 | (dynamic) | -32735 | 32735
| Reference2 | HR | 3 | 2 | 3 | dp depend by the input variables, range is signed word | Int32 | (dynamic) | -32735 | 32735
| Delay On Delay | HR | 5 | 2 | 3 |  | UInt32 | Seconds | 0 | 600
| Delay Off Delay | HR | 7 | 2 | 3 |  | UInt32 | Seconds | 0 | 600
SEQUENCE
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Number
| Step ID | IR | 1 | 1 | 4 |  | UInt16 | Number
| Step delay | IR | 2 | 2 | 4 |  | UInt32 | Seconds
| Automation enable timer | IR | 4 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | Running State: 0 = Stopped 1 = Started 2 = Paused | UInt16 | Unknown Unit
PARAMETERS | Automation enable delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
CAR HEATING
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Unknown Unit
| Feedback STATE | IR | 1 | 1 | 4 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
| Temperature | IR | 2 | 2 | 4 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0 | 7FFFh
| Long Time | IR | 4 | 1 | 4 |  | UInt16 | Seconds | 0 | 36000 | 7FFFh
| Automation enable timer | IR | 5 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | 0=OFF 1=ON | UInt16 | Unknown Unit
PARAMETERS | Lower temperature limit | HR | 2 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0
| Higher temperature limit | HR | 4 | 2 | 3 |  | Int32 | Celsius degrees / Fahreneheit degrees | -50.0 | 150.0
| Automation enable delay | HR | 6 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
PLAYBACK
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF all other bits: reserved | UInt16 | Unknown Unit
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | Running State: 0 = Stopped 1 = Started 2 = Paused | UInt16 | Unknown Unit
| Automation enable delay | HR | 2 | 2 | 3 |  |  | Seconds | 0 | 3540 (59min)
DIMMER
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF bit11 = PIR presence all other bits: reserved | UInt16 | Unknown Unit
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Lux Interval Name | IR | 3 | 1 | 4 | None = -1 Default = 0 Night = 10 Day = 20 | UInt16 | Number | 0 | 5000
| Energy save timer | IR | 4 | 2 | 4 |  | UInt32 | Seconds | 0 | 43200
| Lux | IR | 6 | 2 | 4 |  | UInt32 | Lux | 0 | 20000 | 7FFFFFFFh
| Function STATE | HR | 0 | 1 | 4 | 0..100 = output % | UInt16 | Unknown Unit
PARAMETERS | Energy save delay | HR | 2 | 2 |  |  | UInt32 | Seconds | 0 | 43200
| Lux thereshold | HR | 4 | 1 | 3 |  | UInt16 | Lux | 0 | 20000
| Cloud filter | HR | 5 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Automation enable delay | HR | 6 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Action on esTimer night | HR | 8 | 1 | 3 | -1 = no action 0 = OFF 1 = S1 2 = S2 3 = S3 4 = S4 5 = S5 10..100 = Position % 60001 = trigger sequence1 60002 = trigger sequence2 | Int16 | Unknown Unit
| Action on esTimer day | HR | 9 | 1 | 3 | see Action on esTimer night | Int16 | Unknown Unit
| Action on esTimer without lux | HR | 10 | 1 | 3 | Azioni che l'energy save puo' eseguire quando non e' presente il Luxmetro -1 = no action 0 = OFF 1 = S1 2 = S2 3 = S3 4 = S4 5 = S5 10..100 = Position % | Int16 | Unknown Unit
| Lux action on night | HR | 11 | 1 | 3 | -1 = no action 0 = OFF 1 = S1 2 = S2 3 = S3 4 = S4 5 = S5 10..100 = Position % | Int16 | Percentage
| Lux action on day | HR | 12 | 1 | 3 | see Action on Lux action night | Int16 | Percentage
| Lux Disable Pir during day time | HR | 13 | 1 | 3 | Il luxmetro disabilita il in condizione giorno 0 = False 1 = True | UInt16 | Unknown Unit
| Action on PIR MOV night | HR | 14 | 1 | 3 | Azioni che il Pir puo' eseguire quando e' presente il Luxmetro -1 = no action 0 = OFF 1 = S1 + retrigger 2 = S2 + retrigger 3 = S3 + retrigger 4 = S4 + retrigger 5 = S5 + retrigger 10..100 = Position % + retrigger | Int16 | Percentage
| Action on PIR MOV day | HR | 15 | 1 | 3 | see Action on PIR MOV night | Int16 | Percentage
| Pir Action without lux | HR | 16 | 1 | 3 | Azioni che il Pir puo' eseguire quando non e' presente il Luxmetro -1 = no action 0 = OFF 1 = S1 2 = S2 3 = S3 4 = S4 5 = S5 10..100 = Position % | Int16 | Unknown Unit
| Allow Pir to Switch ON | HR | 17 | 1 | 3 | 0 = False 1 = True | UInt16 | Unknown Unit
| Set S2 | HR | 18 | 1 | 3 |  | UInt16 | Percentage | 10 | 100
| Set S3 | HR | 19 | 1 | 3 |  | UInt16 | Percentage | 10 | 100
| Set S4 | HR | 20 | 1 | 3 |  | UInt16 | Percentage | 10 | 100
| Set S5 | HR | 21 | 1 | 3 |  | UInt16 | Percentage | 10 | 100
DIMMER SEQUENCE
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override RUN bit10 = Override STOP all other bits: reserved | UInt16 | Number
| Step ID | IR | 1 | 1 | 4 |  | UInt16 | Number
| Countdown Timer | IR | 2 | 2 | 4 |  | UInt32 | Seconds | 0 | 599
| Automation enable timer | IR | 4 | 2 | 4 |  | UInt32 | Secons | 0 | 3540 (59min)
| Function STATE | HR | 0 | 1 | 4 | Running State: 0 = Stopped 1 = Started 2 = Paused | UInt16 | Unknown Unit
COMMANDS | SET | HR | 1 | 1 | 3 | 0 = Stop 1 = START 2 = PAUSE/START 1000 = Activate automatism disable (with timeout) 1001 = Deactivate automatism disable
| Automation enable delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
CONST. LIGHT
STATUS | Diagnostic STATE | IR | 0 | 1 | 4 | bit8 = DISABLE bit9 = Override ON bit10 = Override OFF bit11 = PIR presence all other bits: reserved | UInt16 | Unknown Unit
| Automation enable timer | IR | 1 | 2 | 4 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Energy save timer | IR | 3 | 2 | 4 |  | UInt32 | Seconds | 0 | 43200
| Lux read | IR | 5 | 2 | 4 |  | UInt32 | Lux | 0 | 25000
| Lux set | IR | 7 | 2 | 4 |  | UInt32 | Lux | 0 | 25000
| Max lux range | IR | 9 | 2 | 4 |  | UInt32 | Lux | 0 | 25000
| Dimmer % | IR | 11 | 1 | 4 |  | UInt16 | Lux | 0 | 25000
| Function STATE | HR | 0 | 1 | 4 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
PARAMETERS | Energy save delay | HR | 2 | 2 | 3 |  | UInt32 | Seconds | 0 | 43200
| Threshold | HR | 4 | 2 | 3 |  | UInt32 | Lux | MaxLuxRange+20% | 50000
| Cloud filter | HR | 6 | 1 | 3 |  | UInt16 | Seconds | 0 | 600
| Automation enable delay | HR | 7 | 2 | 3 |  | UInt32 | Seconds | 0 | 3540 (59min)
| Action on esTimer | HR | 9 | 1 | 3 | -1 = no action 0 = OFF 1 = S1 2 = S2 3 = S3 4 = S4 5 = S5 6..MaxLuxRange = Lux 30001 = trigger sequence1 30002 = trigger sequence2 | Int16 | Unknown Unit
| Action on PIR MOV | HR | 10 | 1 | 3 | -1 = no action 0 = OFF 1 = S1 2 = S2 3 = S3 4 = S4 5 = S5 6..MaxLuxRange = Lux | Int16 | Lux
| Allow Pir to Switch ON | HR | 11 | 1 | 3 | 0 = False 1 = True | UInt16 | Unknown Unit
| Set S2 | HR | 12 | 1 | 3 |  | UInt16 | Lux | 0 | MaxLuxRange
| Set S3 | HR | 13 | 1 | 3 |  | UInt16 | Lux | 0 | MaxLuxRange
| Set S4 | HR | 14 | 1 | 3 |  | UInt16 | Lux | 0 | MaxLuxRange
| Set S5 | HR | 15 | 1 | 3 |  | UInt16 | Lux | 0 | MaxLuxRange
MULTIGATE
STATUS | Function STATE | HR | 0 | 1 | 4 | 0 = OFF 1 = ON | UInt16 | Unknown Unit
COUNTER
STATUS | Delta value | IR | 0 | 2 | 4 |  | Int32 | (dynamic)
| Feedback STATE | IR | 2 | 1 | 4 |  | UInt16 | Unknown Unit
| Function STATE | HR | 0 | 2 | 4 |  | Int32 | (dynamic)
| Threshold | HR | 4 | 2 | 3 |  | Int32 | (dynamic)

## Info Modbus (debug mode)
| Parameter name | Register type | Relative address (word) | Word lenght Modbus | ModBus Function | Data info | Data type | Measure Unit | min | max | error
ANALOGUE OUTPUT
STATUS | Reset output | IR | 0 | 2 | 4 |  | Int32 | Unknown Unit
| Function STATE | HR | 0 | 2 | 4 |  | Int32 | Unknown Unit
MODBUS GATEWAY
STATUS | Function STATE | HR | 0 | 1 | 4 |  | UInt16 | Unknown Unit
PID CONTROL
STATUS | PID value | IR | 0 | 2 | 4 |  | Int32 | Percentage
| PID input value | IR | 4 | 2 | 4 |  | Int32 | (dynamic)
| Function STATE | HR | 0 | 2 | 4 |  | Int32 | Unknown Unit
PARAMETERS | Setpoint value | HR | 5 | 2 | 3 |  | Int32 | (dynamic)
LINEAR APPROXIMATION
STATUS | Highest input value | IR | 0 | 2 | 4 |  | Int32 | Number
| Lowest input value | IR | 2 | 2 | 4 |  | Int32 | Number
| Average input value linearized + offset | IR | 4 | 2 | 4 |  | Int32 | Number
| A input - B input | IR | 6 | 2 | 4 |  | Int32 | Number
| Lowest linearized value | IR | 8 | 2 | 4 |  | Int32 | Unknown Unit
| Highest linearized value | IR | 10 | 2 | 4 |  | Int32 | Unknown Unit
| Function STATE | HR | 0 | 2 | 4 |  | Int32 | Number
PARAMETERS | Offeset value | HR | 2 | 2 | 4 |  | Int32 | Number

## Modules Maps
Part Number | Indx | Workmode | Measure unit | Start address (Dec) | Lenght | Mult. | * = multiplier set by user
B4X-LS4-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
B5X-LS4-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
B4X-PIR90-U | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
| 3 | LED | - | 3 | UInt16 | 1
B5X-PIR90-U | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
| 3 | LED | - | 3 | UInt16 | 1
BACC-KEYPAD-DC-U | 1 | Bell | - | 0 | UInt16 | 1
| 2 | Code accepted | - | 1 | UInt16 | 1
| 3 | LED | - | 2 | UInt16 | 1
| 4 | LED | - | 3 | UInt16 | 1
| 5 | Buzzer | - | 4 | UInt16 | 1
BDA-INVOL-U | 1 | Switch | - | 0 | UInt16 | 1
BDA-RE13A-U | 1 | Relè | - | 0 | UInt16 | 1
BDB_INCON4_U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
BDB_INCON8_U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Push | - | 4 | UInt16 | 1
| 6 | Push | - | 5 | UInt16 | 1
| 7 | Push | - | 6 | UInt16 | 1
| 8 | Push | - | 7 | UInt16 | 1
BDB_IOCP8_U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
BDB_IOCP8A_U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
BDD-INCON4-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Led | - | 4 | UInt16 | 1
BEW-LS1-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | LED | - | 1 | UInt16 | 1
BEW-LS2-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Led | - | 2 | UInt16 | 1
| 4 | Led | - | 3 | UInt16 | 1
BEW-LS3-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Led | - | 3 | UInt16 | 1
| 5 | Led | - | 4 | UInt16 | 1
| 6 | Led | - | 5 | UInt16 | 1
BEW-LS4-U | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Led | - | 4 | UInt16 | 1
| 6 | Led | - | 5 | UInt16 | 1
| 7 | Led | - | 6 | UInt16 | 1
| 8 | Led | - | 7 | UInt16 | 1
BSB-PIR90-U | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
| 3 | LED | - | 3 | UInt16 | 1
BSD-PIR90-U | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
| 3 | LED | - | 3 | UInt16 | 1
BSF-WAT-U | 1 | Water alarm | - | 0 | UInt16 | 1
BSG-SMOA-U | 1 | Smoke alarm | - | 0 | UInt16 | 1
| 2 | Buzzer | - | 1 | UInt16 | 1
BSG-SMO-U | 1 | Smoke alarm | - | 0 | UInt16 | 1
| 2 | Buzzer | - | 1 | UInt16 | 1
BSH-LUX-U | 1 | Lux | Lux | 0 | Int32 | 1
BSI-TEMANA-U | 1 | Temperature | °C | 0 | Int32 | 0.1
BSI-TEMANB-U | 1 | Temperature | °C | 0 | Int32 | 0.1
BSN-ANE-U | 1 | Wind | m/s | 0 | Int32 | 0.1
BSP-PIR90x-U | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
SH2D500WE230 | 1 | kWh | kWh | 0 | Int32 | 0.1
| 2 | Wdmd | W | 2 | Int32 | 0.1
| 3 | Watt | W | 4 | Int32 | 0.1
| 4 | VA | VA | 6 | Int32 | 0.1
| 5 | var | var | 8 | Int32 | 0.1
| 6 | Ampere | A | 10 | Int32 | 0.001
| 7 | Volt | V | 12 | Int32 | 0.1
| 8 | PF | PF | 14 | Int32 | 0.001
SH2INDI424 | 1 | Switch/Custom | - / Custom | 0 | Int32 | 1/*
| 2 | Switch/Custom | - / Custom | 2 | Int32 | 1/*
| 3 | Switch/Custom | - / Custom | 4 | Int32 | 1/*
| 4 | Switch/Custom | - / Custom | 6 | Int32 | 1/*
SH2RE16A2E230 | 1 | kWh | kWh | 0 | Int32 | 0.1
| 2 | Wdmd | W | 2 | Int32 | 0.1
| 3 | Watt | W | 4 | Int32 | 0.1
| 4 | VA | VA | 6 | Int32 | 0.1
| 5 | var | var | 8 | Int32 | 0.1
| 6 | Ampere | A | 10 | Int32 | 0.001
| 7 | Volt | V | 12 | Int32 | 0.1
| 8 | PF | PF | 14 | Int32 | 0.001
| 9 | Relè | - | 16 | UInt16 | 1
| 10 | Relè | - | 17 | UInt16 | 1
SH2RE16A4 | 1 | Relè | - | 0 | UInt16 | 1
| 2 | Relè | - | 1 | UInt16 | 1
| 3 | Relè | - | 2 | UInt16 | 1
| 4 | Relè | - | 3 | UInt16 | 1
SH2RE1A424 | 1 | Relè | - | 0 | UInt16 | 1
| 2 | Relè | - | 1 | UInt16 | 1
| 3 | Relè | - | 2 | UInt16 | 1
| 4 | Relè | - | 3 | UInt16 | 1
SH2SSTRI424 | 1 | Triac | - | 0 | UInt16 | 1
| 2 | Triac | - | 1 | UInt16 | 1
| 3 | Triac | - | 2 | UInt16 | 1
| 4 | Triac | - | 3 | UInt16 | 1
SH-8158 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
SHA4XLS4P90L | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Lux | Lux | 4 | Int32 | 1
| 6 | Pir | - | 6 | UInt16 | 1
| 7 | Alarm | - | 8 | UInt16 | 1
| 8 | LED | - | 9 | UInt16 | 1
SHA4XLS4TH | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Humidity | %RH | 4 | Int32 | 0.1
| 6 | Temperature | °C | 6 | Int32 | 0.1
| 7 | LED | - | 8 | UInt16 | 1
| 8 | LED | - | 9 | UInt16 | 1
| 9 | LED | - | 10 | UInt16 | 1
| 10 | LED | - | 11 | UInt16 | 1
SHA4XP150 | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
| 3 | LED | - | 3 | UInt16 | 1
SHA4XP150L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Luxmeter | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHA4XP90L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Luxmeter | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHA4XTEMDIS | 1 | Troom | °C | 0 | Int32 | 0.1
| 2 | Tauxiliary | °C | 2 | Int32 | 0.1
SHA4XWLS4 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
SHDWRE16AE230 | 1 | kWh | kWh | 0 | Int32 | 0.1
| 2 | Wdmd | W | 2 | Int32 | 0.1
| 3 | Watt | W | 4 | Int32 | 0.1
| 4 | VA | VA | 6 | Int32 | 0.1
| 5 | var | var | 8 | Int32 | 0.1
| 6 | Ampere | A | 10 | Int32 | 0.001
| 7 | Volt | V | 12 | Int32 | 0.1
| 8 | PF | PF | 14 | Int32 | 0.001
| 9 | Relè | - | 16 | UInt16 | 1
SHDWWISEN | 1 | Switch | - | 0 | UInt16 | 1
SHDWWISENIN1 | 1 | Switch | - | 0 | UInt16 | 1
| 2 | Switch | - | 1 | UInt16 | 1
SHE5XLS4P90L | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Lux | Lux | 4 | Int32 | 1
| 6 | Pir | - | 6 | UInt16 | 1
| 7 | Alarm | - | 8 | UInt16 | 1
| 8 | LED | - | 9 | UInt16 | 1
SHE5XLS4TH | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Humidity | %RH | 4 | Int32 | 0.1
| 6 | Temperature | °C | 6 | Int32 | 0.1
| 7 | LED | - | 8 | UInt16 | 1
| 8 | LED | - | 9 | UInt16 | 1
| 9 | LED | - | 10 | UInt16 | 1
| 10 | LED | - | 11 | UInt16 | 1
SHE5XP150 | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Alarm | - | 2 | UInt16 | 1
| 3 | LED | - | 3 | UInt16 | 1
SHE5XP150L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Luxmeter | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHE5XP90L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Luxmeter | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHE5XTEMDIS | 1 | Troom | °C | 0 | Int32 | 0.1
| 2 | Tauxiliary | °C | 2 | Int32 | 0.1
SHE5XWLS4 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
SHEKxTEMDIS | 1 | Troom | °C | 0 | Int32 | 0.1
| 2 | Tauxiliary | °C | 2 | Int32 | 0.1
SHG060BLS4 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Temperature | °C | 4 | Int32 | 0.1
| 6 | LED | - | 6 | UInt16 | 1
| 7 | LED | - | 7 | UInt16 | 1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
SHG060BSLD | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
SHG060BSLT | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | TRoom | °C | 4 | Int32 | 0.1
| 6 | LED | - | 6 | UInt16 | 1
| 7 | LED | - | 7 | UInt16 | 1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
SHG060WLS4 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Temperature | °C | 4 | Int32 | 0.1
| 6 | LED | - | 6 | UInt16 | 1
| 7 | LED | - | 7 | UInt16 | 1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
SHG060WSLD | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
SHG060WSLT | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | TRoom | °C | 4 | Int32 | 0.1
| 6 | LED | - | 6 | UInt16 | 1
| 7 | LED | - | 7 | UInt16 | 1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
SHG503BLS6 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Push | - | 4 | UInt16 | 1
| 6 | Push | - | 5 | UInt16 | 1
| 7 | Temperature | °C | 6 | Int32 | 0.1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
| 10 | LED | - | 10 | UInt16 | 1
| 11 | LED | - | 11 | UInt16 | 1
| 12 | LED | - | 12 | UInt16 | 1
| 13 | LED | - | 13 | UInt16 | 1
SHG503BSLD | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
SHG503BSLT | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | TRoom | °C | 4 | Int32 | 0.1
| 6 | LED | - | 6 | UInt16 | 1
| 7 | LED | - | 7 | UInt16 | 1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
SHG503WLS6 | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | Push | - | 4 | UInt16 | 1
| 6 | Push | - | 5 | UInt16 | 1
| 7 | Temperature | °C | 6 | Int32 | 0.1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
| 10 | LED | - | 10 | UInt16 | 1
| 11 | LED | - | 11 | UInt16 | 1
| 12 | LED | - | 12 | UInt16 | 1
| 13 | LED | - | 13 | UInt16 | 1
SHG503WSLD | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | LED | - | 4 | UInt16 | 1
| 6 | LED | - | 5 | UInt16 | 1
| 7 | LED | - | 6 | UInt16 | 1
| 8 | LED | - | 7 | UInt16 | 1
SHG503WSLT | 1 | Push | - | 0 | UInt16 | 1
| 2 | Push | - | 1 | UInt16 | 1
| 3 | Push | - | 2 | UInt16 | 1
| 4 | Push | - | 3 | UInt16 | 1
| 5 | TRoom | °C | 4 | Int32 | 0.1
| 6 | LED | - | 6 | UInt16 | 1
| 7 | LED | - | 7 | UInt16 | 1
| 8 | LED | - | 8 | UInt16 | 1
| 9 | LED | - | 9 | UInt16 | 1
SHPINA224 | 1 | Analogue | Custom | 0 | Int32 | *
| 2 | Analogue | Custom | 2 | Int32 | *
SHPINCNT4 | 1 | Switch/Custom | - / Custom | 0 | Int32 | 1/*
| 2 | Switch/Custom | - / Custom | 2 | Int32 | 1/*
| 3 | Switch/Custom | - / Custom | 4 | Int32 | 1/*
| 4 | Switch/Custom | - / Custom | 6 | Int32 | 1/*
SHPINCNTS04 | 1 | Switch/Custom | - / Custom | 0 | Int32 | 1/*
| 2 | Switch/Custom | - / Custom | 2 | Int32 | 1/*
| 3 | Switch/Custom | - / Custom | 4 | Int32 | 1/*
| 4 | Switch/Custom | - / Custom | 6 | Int32 | 1/*
SHPINNI2 | 1 | Thermistor | °C | 0 | Int32 | 0.1
| 2 | Thermistor | °C | 2 | Int32 | 0.1
SHPINT1P1 | 1 | Thermistor | °C | 0 | Int32 | 0.1
| 2 | Analogue | % | 2 | Int32 | 0.1
SHPINV2T1P124 | 1 | Analogue | Custom | 0 | Int32 | *
| 2 | Analogue | Custom | 2 | Int32 | *
| 3 | Thermistor | °C | 4 | Int32 | 0.1
| 4 | Analogue | Custom | 6 | Int32 | *
SHPINV324 | 1 | Analogue | Custom | 0 | Int32 | *
| 2 | Analogue | Custom | 2 | Int32 | *
| 3 | Analogue | Custom | 4 | Int32 | *
SHPOUTV224 | 1 | Analogue | Custom | 0 | Int32 | *
| 2 | Analogue | Custom | 2 | Int32 | *
SHSBP90L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Lux | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHSDP90L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Lux | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHSPP90Lx | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Lux | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
| 4 | LED | - | 5 | UInt16 | 1
SHSQP360L | 1 | Pir | - | 0 | UInt16 | 1
| 2 | Lux | Lux | 2 | Int32 | 1
| 3 | Alarm | - | 4 | UInt16 | 1
SHSUCOT | 1 | CO2 | ppm | 0 | Int32 | 1
| 2 | Temperature | °C | 2 | Int32 | 0.1
SHSUCOTD | 1 | CO2 | ppm | 0 | Int32 | 1
| 2 | Temperature | °C | 2 | Int32 | 0.1
SHSUCOTH | 1 | CO2 | ppm | 0 | Int32 | 1
| 2 | Temperature | °C | 2 | Int32 | 0.1
| 3 | Humidity | %RH | 4 | Int32 | 0.1
SHSUCOTHD | 1 | CO2 | ppm | 0 | Int32 | 1
| 2 | Temperature | °C | 2 | Int32 | 0.1
| 3 | Humidity | %RH | 4 | Int32 | 0.1
SHSUCOTHL | 1 | CO2 | ppm | 0 | Int32 | 1
| 2 | Temperature | °C | 2 | Int32 | 0.1
| 3 | Humidity | %RH | 4 | Int32 | 0.1
SHSUCOTL | 1 | CO2 | ppm | 0 | Int32 | 1
| 2 | Temperature | °C | 2 | Int32 | 0.1
SHSUT | 1 | Temperature | °C | 0 | Int32 | 0.1
SHSUTD | 1 | Temperature | °C | 0 | Int32 | 0.1
SHSUTH | 1 | Temperature | °C | 0 | Int32 | 0.1
| 2 | Humidity | %RH | 2 | Int32 | 0.1
SHSUTHD | 1 | Temperature | °C | 0 | Int32 | 0.1
| 2 | Humidity | %RH | 2 | Int32 | 0.1
EM2172DAV53XOSPFAD | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM2172DAV53XOSPFAP | 2 | Vl1n | V | 2 | Int32 | 0.1
EM2172DAV53XOSPFBD | 3 | Vl2n | V | 4 | Int32 | 0.1
EM2172DAV53XOSPFBP | 4 | Vl3n | V | 6 | Int32 | 0.1
EM2172DAV53XOSX | 5 | Vllsys | V | 8 | Int32 | 0.1
EM2172DAV63XOSPFAD | 6 | Vl1l2 | V | 10 | Int32 | 0.1
EM2172DAV63XOSPFAP | 7 | Vl2l3 | V | 12 | Int32 | 0.1
EM2172DAV63XOSPFBD | 8 | Vl3l1 | V | 14 | Int32 | 0.1
EM2172DAV63XOSPFBP | 9 | Al1 | A | 16 | Int32 | 0.001
EM2172DAV63XOSX | 10 | Al2 | A | 18 | Int32 | 0.001
EM2172VMV53XOSX | 11 | Al3 | A | 20 | Int32 | 0.001
EM2172VMV63XOSX | 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | PSeq | - | 50 | Int32 | 0.001
| 27 | kvarh | kvarh | 52 | Int32 | 0.1
| 28 | PFsys | PF | 54 | Int32 | 0.001
| 29 | PFl1 | PF | 56 | Int32 | 0.001
| 30 | PFl2 | PF | 58 | Int32 | 0.001
| 31 | PFl3 | PF | 60 | Int32 | 0.001
EM2172RVV23XOSX | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM2172RVV33XOSX | 2 | Vl1n | V | 2 | Int32 | 0.1
EM2172RVV53XOSX | 3 | Vl2n | V | 4 | Int32 | 0.1
| 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | PSeq | - | 50 | Int32 | 0.001
| 27 | kvarh | kvarh | 52 | Int32 | 0.1
| 28 | PFsys | PF | 54 | Int32 | 0.001
| 29 | PFl1 | PF | 56 | Int32 | 0.001
| 30 | PFl2 | PF | 58 | Int32 | 0.001
| 31 | PFl3 | PF | 60 | Int32 | 0.001
EM23DINAV23XS1PFA | 1 | Vl1n | V | 0 | Int32 | 0.1
EM23DINAV23XS1PFB | 2 | Vl2n | V | 2 | Int32 | 0.1
EM23DINAV23XS1X | 3 | Vl3n | V | 4 | Int32 | 0.1
EM23DINAV93XS1PFA | 4 | Al1 | A | 6 | Int32 | 0.001
EM23DINAV93XS1PFB | 5 | Al2 | A | 8 | Int32 | 0.001
EM23DINAV93XS1X | 6 | Al3 | A | 10 | Int32 | 0.001
| 7 | kWsys | W | 12 | Int32 | 0.1
| 8 | kWhac | kWh | 14 | Int32 | 0.1
| 9 | PSeq | - | 16 | Int32 | 0.001
| 10 | kvarsys | var | 18 | Int32 | 0.1
| 11 | kvarh | kvarh | 20 | Int32 | 0.1
EM24DINAV23XISPFA | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM24DINAV23XISPFB | 2 | Vl1n | V | 2 | Int32 | 0.1
EM24DINAV23XISX | 3 | Vl2n | V | 4 | Int32 | 0.1
| 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | kvarh | kvarh | 50 | Int32 | 0.1
| 27 | kvarhn | kvarh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | kWhl1 | kWh | 72 | Int32 | 0.1
| 38 | kWhl2 | kWh | 74 | Int32 | 0.1
| 39 | kWhl3 | kWh | 76 | Int32 | 0.1
| 40 | DMDWsys | W | 78 | Int32 | 0.1
| 41 | DMDVAsys | VA | 80 | Int32 | 0.1
| 42 | DMDWsysMax | W | 82 | Int32 | 0.1
| 43 | DMDVAsysMax | VA | 84 | Int32 | 0.1
| 44 | DMDAMax | A | 86 | Int32 | 0.001
| 45 | kWhPar | kWh | 88 | Int32 | 0.1
| 46 | kvarhPar | kvarh | 90 | Int32 | 0.1
| 47 | kWht1 | kWh | 92 | Int32 | 0.1
| 48 | kWht2 | kWh | 94 | Int32 | 0.1
| 49 | kWht3 | kWh | 96 | Int32 | 0.1
| 50 | kWht4 | kWh | 98 | Int32 | 0.1
| 51 | kvarht1 | kvarh | 100 | Int32 | 0.1
| 52 | kvarht2 | kvarh | 102 | Int32 | 0.1
| 53 | kvarht3 | kvarh | 104 | Int32 | 0.1
| 54 | kvarht4 | kvarh | 106 | Int32 | 0.1
| 55 | hour | HH | 108 | Int32 | 0.01
EM24DINAV53DISPFA | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM24DINAV53DISPFB | 2 | Vl1n | V | 2 | Int32 | 0.1
EM24DINAV53DISX | 3 | Vl2n | V | 4 | Int32 | 0.1
EM24DINAV53LISX | 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | kvarh | kvarh | 50 | Int32 | 0.1
| 27 | kvarhn | kvarh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | kWhl1 | kWh | 72 | Int32 | 0.1
| 38 | kWhl2 | kWh | 74 | Int32 | 0.1
| 39 | kWhl3 | kWh | 76 | Int32 | 0.1
| 40 | DMDWsys | W | 78 | Int32 | 0.1
| 41 | DMDVAsys | VA | 80 | Int32 | 0.1
| 42 | DMDWsysMax | W | 82 | Int32 | 0.1
| 43 | DMDVAsysMax | VA | 84 | Int32 | 0.1
| 44 | DMDAMax | A | 86 | Int32 | 0.001
| 45 | kWhPar | kWh | 88 | Int32 | 0.1
| 46 | kvarhPar | kvarh | 90 | Int32 | 0.1
| 47 | kWht1 | kWh | 92 | Int32 | 0.1
| 48 | kWht2 | kWh | 94 | Int32 | 0.1
| 49 | kWht3 | kWh | 96 | Int32 | 0.1
| 50 | kWht4 | kWh | 98 | Int32 | 0.1
| 51 | kvarht1 | kvarh | 100 | Int32 | 0.1
| 52 | kvarht2 | kvarh | 102 | Int32 | 0.1
| 53 | kvarht3 | kvarh | 104 | Int32 | 0.1
| 54 | kvarht4 | kvarh | 106 | Int32 | 0.1
| 55 | hour | HH | 108 | Int32 | 0.01
EM24DINAV63DISX | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM24DINAV63LISX | 2 | Vl1n | V | 2 | Int32 | 0.1
| 3 | Vl2n | V | 4 | Int32 | 0.1
| 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | kvarh | kvarh | 50 | Int32 | 0.1
| 27 | kvarhn | kvarh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | kWhl1 | kWh | 72 | Int32 | 0.1
| 38 | kWhl2 | kWh | 74 | Int32 | 0.1
| 39 | kWhl3 | kWh | 76 | Int32 | 0.1
| 40 | DMDWsys | W | 78 | Int32 | 0.1
| 41 | DMDVAsys | VA | 80 | Int32 | 0.1
| 42 | DMDWsysMax | W | 82 | Int32 | 0.1
| 43 | DMDVAsysMax | VA | 84 | Int32 | 0.1
| 44 | DMDAMax | A | 86 | Int32 | 0.001
| 45 | kWhPar | kWh | 88 | Int32 | 0.1
| 46 | kvarhPar | kvarh | 90 | Int32 | 0.1
| 47 | kWht1 | kWh | 92 | Int32 | 0.1
| 48 | kWht2 | kWh | 94 | Int32 | 0.1
| 49 | kWht3 | kWh | 96 | Int32 | 0.1
| 50 | kWht4 | kWh | 98 | Int32 | 0.1
| 51 | kvarht1 | kvarh | 100 | Int32 | 0.1
| 52 | kvarht2 | kvarh | 102 | Int32 | 0.1
| 53 | kvarht3 | kvarh | 104 | Int32 | 0.1
| 54 | kvarht4 | kvarh | 106 | Int32 | 0.1
| 55 | hour | HH | 108 | Int32 | 0.01
EM24DINAV93XISPFA | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM24DINAV93XISPFB | 2 | Vl1n | V | 2 | Int32 | 0.1
EM24DINAV93XISX | 3 | Vl2n | V | 4 | Int32 | 0.1
| 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | kvarh | kvarh | 50 | Int32 | 0.1
| 27 | kvarhn | kvarh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | kWhl1 | kWh | 72 | Int32 | 0.1
| 38 | kWhl2 | kWh | 74 | Int32 | 0.1
| 39 | kWhl3 | kWh | 76 | Int32 | 0.1
| 40 | DMDWsys | W | 78 | Int32 | 0.1
| 41 | DMDVAsys | VA | 80 | Int32 | 0.1
| 42 | DMDWsysMax | W | 82 | Int32 | 0.1
| 43 | DMDVAsysMax | VA | 84 | Int32 | 0.1
| 44 | DMDAMax | A | 86 | Int32 | 0.001
| 45 | kWhPar | kWh | 88 | Int32 | 0.1
| 46 | kvarhPar | kvarh | 90 | Int32 | 0.1
| 47 | kWht1 | kWh | 92 | Int32 | 0.1
| 48 | kWht2 | kWh | 94 | Int32 | 0.1
| 49 | kWht3 | kWh | 96 | Int32 | 0.1
| 50 | kWht4 | kWh | 98 | Int32 | 0.1
| 51 | kvarht1 | kvarh | 100 | Int32 | 0.1
| 52 | kvarht2 | kvarh | 102 | Int32 | 0.1
| 53 | kvarht3 | kvarh | 104 | Int32 | 0.1
| 54 | kvarht4 | kvarh | 106 | Int32 | 0.1
| 55 | hour | HH | 108 | Int32 | 0.01
EM2696AV53HI3S1PFA | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM2696AV53HI3S1PFB | 2 | Vl1n | V | 2 | Int32 | 0.1
EM2696AV53HI3S1XX | 3 | Vl2n | V | 4 | Int32 | 0.1
EM2696AV53HO1S1PFA | 4 | Vl3n | V | 6 | Int32 | 0.1
EM2696AV53HO1S1PFB | 5 | Vllsys | V | 8 | Int32 | 0.1
EM2696AV53HO1S1XX | 6 | Vl1l2 | V | 10 | Int32 | 0.1
EM2696AV53HO3S1PFA | 7 | Vl2l3 | V | 12 | Int32 | 0.1
EM2696AV53HO3S1PFB | 8 | Vl3l1 | V | 14 | Int32 | 0.1
EM2696AV53HO3S1XX | 9 | Al1 | A | 16 | Int32 | 0.001
EM2696AV53HR2S1PFA | 10 | Al2 | A | 18 | Int32 | 0.001
EM2696AV53HR2S1PFB | 11 | Al3 | A | 20 | Int32 | 0.001
EM2696AV53HR2S1XX | 12 | kWl1 | w | 22 | Int32 | 0.1
| 13 | kWl2 | w | 24 | Int32 | 0.1
| 14 | kWl3 | w | 26 | Int32 | 0.1
| 15 | kWsys | w | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | kvarh | kvarh | 50 | Int32 | 0.1
| 27 | kvarhn | kvarh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | kWhl1 | kWh | 72 | Int32 | 0.1
| 38 | kWhl2 | kWh | 74 | Int32 | 0.1
| 39 | kWhl3 | kWh | 76 | Int32 | 0.1
| 40 | THDAl1 | % | 78 | Int32 | 0.1
| 41 | THDAl2 | % | 80 | Int32 | 0.1
| 42 | THDAl3 | % | 82 | Int32 | 0.1
| 43 | THDVl1n | % | 84 | Int32 | 0.1
| 44 | THDVl2n | % | 86 | Int32 | 0.1
| 45 | THDVl3n | % | 88 | Int32 | 0.1
| 46 | DMDWsys | W | 90 | Int32 | 0.1
| 47 | DMDVAsys | VA | 92 | Int32 | 0.1
| 48 | DMDWsysMax | W | 94 | Int32 | 0.1
| 49 | DMDVAsysMax | VA | 96 | Int32 | 0.1
| 50 | DMDAMax | A | 98 | Int32 | 0.001
| 51 | kWhPar | kWh | 100 | Int32 | 0.1
| 52 | kvarhPar | kvarh | 102 | Int32 | 0.1
| 53 | kWht1 | kWh | 104 | Int32 | 0.1
| 54 | kWht2 | kWh | 106 | Int32 | 0.1
| 55 | kWht3 | kWh | 108 | Int32 | 0.1
| 56 | kWht4 | kWh | 110 | Int32 | 0.1
| 57 | kvarht1 | kvarh | 112 | Int32 | 0.1
| 58 | kvarht2 | kvarh | 114 | Int32 | 0.1
| 59 | kvarht3 | kvarh | 116 | Int32 | 0.1
| 60 | kvarht4 | kvarh | 118 | Int32 | 0.1
| 61 | hour | HH | 120 | Int32 | 0.01
| 62 | Al1DMD | A | 122 | Int32 | 0.001
| 63 | Al2DMD | A | 124 | Int32 | 0.001
| 64 | Al3DMD | A | 126 | Int32 | 0.001
| 65 | THDVl1l2 | % | 128 | Int32 | 0.1
| 66 | THDVl2l3 | % | 130 | Int32 | 0.1
| 67 | THDVl3l1 | % | 132 | Int32 | 0.1
EM2696AV63HI3S1PFA | 1 | Vlnsys | V | 0 | Int32 | 0.1
EM2696AV63HI3S1PFB | 2 | Vl1n | V | 2 | Int32 | 0.1
EM2696AV63HI3S1XX | 3 | Vl2n | V | 4 | Int32 | 0.1
EM2696AV63HO1S1PFA | 4 | Vl3n | V | 6 | Int32 | 0.1
EM2696AV63HO1S1PFB | 5 | Vllsys | V | 8 | Int32 | 0.1
EM2696AV63HO1S1XX | 6 | Vl1l2 | V | 10 | Int32 | 0.1
EM2696AV63HO3S1PFA | 7 | Vl2l3 | V | 12 | Int32 | 0.1
EM2696AV63HO3S1PFB | 8 | Vl3l1 | V | 14 | Int32 | 0.1
EM2696AV63HO3S1XX | 9 | Al1 | A | 16 | Int32 | 0.001
EM2696AV63HR2S1PFA | 10 | Al2 | A | 18 | Int32 | 0.001
EM2696AV63HR2S1PFB | 11 | Al3 | A | 20 | Int32 | 0.001
EM2696AV63HR2S1XX | 12 | kWl1 | w | 22 | Int32 | 0.1
| 13 | kWl2 | w | 24 | Int32 | 0.1
| 14 | kWl3 | w | 26 | Int32 | 0.1
| 15 | kWsys | w | 28 | Int32 | 0.1
| 16 | kWhac | kWh | 30 | Int32 | 0.1
| 17 | kVAsys | VA | 32 | Int32 | 0.1
| 18 | kVAl1 | VA | 34 | Int32 | 0.1
| 19 | kVAl2 | VA | 36 | Int32 | 0.1
| 20 | kVAl3 | VA | 38 | Int32 | 0.1
| 21 | kvarsys | var | 40 | Int32 | 0.1
| 22 | kvarl1 | var | 42 | Int32 | 0.1
| 23 | kvarl2 | var | 44 | Int32 | 0.1
| 24 | kvarl3 | var | 46 | Int32 | 0.1
| 25 | Hz | Hz | 48 | Int32 | 0.1
| 26 | kvarh | kvarh | 50 | Int32 | 0.1
| 27 | kvarhn | kvarh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | kWhl1 | kWh | 72 | Int32 | 0.1
| 38 | kWhl2 | kWh | 74 | Int32 | 0.1
| 39 | kWhl3 | kWh | 76 | Int32 | 0.1
| 40 | THDAl1 | % | 78 | Int32 | 0.1
| 41 | THDAl2 | % | 80 | Int32 | 0.1
| 42 | THDAl3 | % | 82 | Int32 | 0.1
| 43 | THDVl1n | % | 84 | Int32 | 0.1
| 44 | THDVl2n | % | 86 | Int32 | 0.1
| 45 | THDVl3n | % | 88 | Int32 | 0.1
| 46 | DMDWsys | W | 90 | Int32 | 0.1
| 47 | DMDVAsys | VA | 92 | Int32 | 0.1
| 48 | DMDWsysMax | W | 94 | Int32 | 0.1
| 49 | DMDVAsysMax | VA | 96 | Int32 | 0.1
| 50 | DMDAMax | A | 98 | Int32 | 0.001
| 51 | kWhPar | kWh | 100 | Int32 | 0.1
| 52 | kvarhPar | kvarh | 102 | Int32 | 0.1
| 53 | kWht1 | kWh | 104 | Int32 | 0.1
| 54 | kWht2 | kWh | 106 | Int32 | 0.1
| 55 | kWht3 | kWh | 108 | Int32 | 0.1
| 56 | kWht4 | kWh | 110 | Int32 | 0.1
| 57 | kvarht1 | kvarh | 112 | Int32 | 0.1
| 58 | kvarht2 | kvarh | 114 | Int32 | 0.1
| 59 | kvarht3 | kvarh | 116 | Int32 | 0.1
| 60 | kvarht4 | kvarh | 118 | Int32 | 0.1
| 61 | hour | HH | 120 | Int32 | 0.01
| 62 | Al1DMD | A | 122 | Int32 | 0.001
| 63 | Al2DMD | A | 124 | Int32 | 0.001
| 64 | Al3DMD | A | 126 | Int32 | 0.001
| 65 | THDVl1l2 | % | 128 | Int32 | 0.1
| 66 | THDVl2l3 | % | 130 | Int32 | 0.1
| 67 | THDVl3l1 | % | 132 | Int32 | 0.1
EM33DINAV33XXSPF | 1 | Vl1n | V | 0 | Int32 | 0.1
EM33DINAV33XXSX | 2 | Vl2n | V | 2 | Int32 | 0.1
| 3 | Vl3n | V | 4 | Int32 | 0.1
| 4 | Al1 | A | 6 | Int32 | 0.001
| 5 | Al2 | A | 8 | Int32 | 0.001
| 6 | Al3 | A | 10 | Int32 | 0.001
| 7 | kWsys | W | 12 | Int32 | 0.1
| 8 | kWhac | kWh | 14 | Int32 | 0.1
| 9 | PSeq | - | 16 | Int32 | 0.001
SHOWEAGPS | 1 | tExt | °C | 0 | Int32 | 0.1
| 2 | sunSouth | Lux | 2 | Int32 | 1
| 3 | sunWest | Lux | 4 | Int32 | 1
| 4 | sunEast | Lux | 6 | Int32 | 1
| 5 | light | Lux | 8 | Int32 | 1
| 6 | wind | m/s | 10 | Int32 | 0.1
| 7 | gps_rtc | - | 12 | Int32 | 0.001
| 8 | rain_info | - | 14 | Int32 | 0.001
| 9 | azim | ° | 16 | Int32 | 0.1
| 10 | elev | ° | 18 | Int32 | 0.1
| 11 | long | ° | 20 | Int32 | 0.1
| 12 | lat | ° | 22 | Int32 | 0.1
WM30 | 1 | Vlnsys | V | 0 | Int32 | 0.1
| 2 | Vl1n | V | 2 | Int32 | 0.1
| 3 | Vl2n | V | 4 | Int32 | 0.1
| 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kVAsys | VA | 30 | Int32 | 0.1
| 17 | kVAl1 | VA | 32 | Int32 | 0.1
| 18 | kVAl2 | VA | 34 | Int32 | 0.1
| 19 | kVAl3 | VA | 36 | Int32 | 0.1
| 20 | kvarsys | var | 38 | Int32 | 0.1
| 21 | kvarl1 | var | 40 | Int32 | 0.1
| 22 | kvarl2 | var | 42 | Int32 | 0.1
| 23 | kvarl3 | var | 44 | Int32 | 0.1
| 24 | Hz | Hz | 46 | Int32 | 0.1
| 25 | kvarh | kvarh | 48 | Int32 | 0.1
| 26 | kvarhn | kvarh | 50 | Int32 | 0.1
| 27 | kWhac | kWh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | THDAl1 | % | 66 | Int32 | 0.1
| 35 | THDAl2 | % | 68 | Int32 | 0.1
| 36 | THDAl3 | % | 70 | Int32 | 0.1
| 37 | THDVl1n | % | 72 | Int32 | 0.1
| 38 | THDVl2n | % | 74 | Int32 | 0.1
| 39 | THDVl3n | % | 76 | Int32 | 0.1
| 40 | DMDWsys | W | 78 | Int32 | 0.1
WM40 | 1 | Vlnsys | V | 0 | Int32 | 0.1
| 2 | Vl1n | V | 2 | Int32 | 0.1
| 3 | Vl2n | V | 4 | Int32 | 0.1
| 4 | Vl3n | V | 6 | Int32 | 0.1
| 5 | Vllsys | V | 8 | Int32 | 0.1
| 6 | Vl1l2 | V | 10 | Int32 | 0.1
| 7 | Vl2l3 | V | 12 | Int32 | 0.1
| 8 | Vl3l1 | V | 14 | Int32 | 0.1
| 9 | Al1 | A | 16 | Int32 | 0.001
| 10 | Al2 | A | 18 | Int32 | 0.001
| 11 | Al3 | A | 20 | Int32 | 0.001
| 12 | kWl1 | W | 22 | Int32 | 0.1
| 13 | kWl2 | W | 24 | Int32 | 0.1
| 14 | kWl3 | W | 26 | Int32 | 0.1
| 15 | kWsys | W | 28 | Int32 | 0.1
| 16 | kVAsys | VA | 30 | Int32 | 0.1
| 17 | kVAl1 | VA | 32 | Int32 | 0.1
| 18 | kVAl2 | VA | 34 | Int32 | 0.1
| 19 | kVAl3 | VA | 36 | Int32 | 0.1
| 20 | kvarsys | var | 38 | Int32 | 0.1
| 21 | kvarl1 | var | 40 | Int32 | 0.1
| 22 | kvarl2 | var | 42 | Int32 | 0.1
| 23 | kvarl3 | var | 44 | Int32 | 0.1
| 24 | Hz | Hz | 46 | Int32 | 0.1
| 25 | kvarh | kvarh | 48 | Int32 | 0.1
| 26 | kvarhn | kvarh | 50 | Int32 | 0.1
| 27 | kWhac | kWh | 52 | Int32 | 0.1
| 28 | kWhacn | kWh | 54 | Int32 | 0.1
| 29 | PFsys | PF | 56 | Int32 | 0.001
| 30 | PFl1 | PF | 58 | Int32 | 0.001
| 31 | PFl2 | PF | 60 | Int32 | 0.001
| 32 | PFl3 | PF | 62 | Int32 | 0.001
| 33 | PSeq | - | 64 | Int32 | 0.001
| 34 | counter1 | - | 66 | Int32 | *
| 35 | counter2 | - | 68 | Int32 | *
| 36 | counter3 | - | 70 | Int32 | *
| 37 | THDAl1 | % | 72 | Int32 | 0.1
| 38 | THDAl2 | % | 74 | Int32 | 0.1
| 39 | THDAl3 | % | 76 | Int32 | 0.1
| 40 | THDVl1n | % | 78 | Int32 | 0.1
| 41 | THDVl2n | % | 80 | Int32 | 0.1
| 42 | THDVl3n | % | 82 | Int32 | 0.1
| 43 | DMDWsys | W | 84 | Int32 | 0.1
| 44 | DMDWsysMax | W | 86 | Int32 | 0.1
VMUEAV00XXXX | 1 | V | V | 0 | Int32 | 0.1
| 2 | A | A | 2 | Int32 | 0.001
| 3 | kWdc | W | 4 | Int32 | 0.1
| 4 | kWhdc | kWh | 6 | Int32 | 0.1
| 5 | Wmax | W | 8 | Int32 | 0.1
| 6 | Wmin | W | 10 | Int32 | 0.1
| 7 | Vmin | V | 12 | Int32 | 0.1
| 8 | Vmax | V | 14 | Int32 | 0.1
VMUEAV10XXXX | 1 | V | V | 0 | Int32 | 0.1
| 2 | A | A | 2 | Int32 | 0.001
| 3 | kWdc | W | 4 | Int32 | 0.1
| 4 | kWhdc | kWh | 6 | Int32 | 0.1
| 5 | Wmax | W | 8 | Int32 | 0.1
| 6 | Wmin | W | 10 | Int32 | 0.1
| 7 | Vmin | V | 12 | Int32 | 0.1
| 8 | Vmax | V | 14 | Int32 | 0.1